## setup
time step duration | 15 | min
horizon | 8 | steps
profiles are used in cycles: | that means, at the end of the profile for the forecasts the values of the beginning are used
simulation time: | 8 | hours
GrdBuyCost and GrdSellCost (means electricity buy and sell costs) are the same for both buildings
GenCosts (gas prices) are the same for both buildings

## SF1_devices
Demand 1 | DEMND01 | Heat Demand
PrimSect |  |  | "heat" | - | string
DemandFC |  |  | time variable | kW | array
EffHtNetReceive |  |  | 0 | 1/(100m) | scalar | for heat network; 0 as no heat network
GrdBuyCost |  |  | 0 | €/kWh | array | for electric grid; 0 as this is heat demand
GrdSellCost |  |  | 0 | €/kWh | array | for electric grid; 0 as this is heat demand
GrdBuyCO2 |  |  | 0 | g/kWh | array | for electric grid; 0 as this is heat demand
GrdSellCO2 |  |  | 0 | g/kWh | array | for electric grid; 0 as this is heat demand
Demand 2 | DEMND02 | Electricity Demand
PrimSect |  |  | "elec" | [-] | string
DemandFC |  |  | time variable | kW | array
EffHtNetReceive |  |  | 0 | 1/(100m) | scalar | for heat network; 0 as this is electricity demand
GrdBuyCost |  |  | time variable | €/kWh | array | for electric grid
GrdSellCost |  |  | time variable | €/kWh | array | for electric grid
GrdBuyCO2 |  |  | 0 | g/kWh | array | for electric grid; 0 as CO2 optimization is not used
GrdSellCO2 |  |  | 0 | g/kWh | array | for electric grid; 0 as CO2 optimization is not used
CHP | COUPL01 | BHKW
PrimSect |  |  | "heat" | [-] | string
SecdSect |  |  | "elec" | [-] | string
EffPrim |  |  | 0.723 | [-] | scalar
EffSecd |  |  | 0.278 | [-] | scalar
MinPower |  |  | 5 | kW | scalar
MaxPower |  |  | 5 | kW | scalar
GenCosts |  |  | time variable | €/kWh | array
CO2PerKWh |  |  | 0 | g/kWh | array | 0 as CO2 optimization is not used
Storage | STRGE01 | thermal storage
PrimSect |  |  | heat | [-] | string
Capacity |  |  | 62.94 | kWh | scalar | 773.6 l, T_max = 90°C, T_ref = 20°C, cp= 4.184 kJ/(kg*K), rho=100kg/m³
EffPrim |  |  | 0.97 | [-] | scalar
DisEffPrim |  |  | 0.97 | [-] | scalar
MaxPowerIn |  |  | 5 | kW | scalar
MaxPower |  |  | 5 | kW | scalar
StorLossPD |  |  | 0.021 | fraction of SOC per hour | scalar | cap = 62.94 kWh; losses = 24 kWh in 24 h beginning with 75% SOC
CO2PerKWh |  |  | -0.00012 | g/kWh | array
SOCminHOR |  |  | 0.5 | [-] | scalar | minimal SOC at end of horizon
PrimEnCost |  |  | 0 | €/kWh | scalar | not used
SOC_init |  |  | 0.75 | [-] | scalar | only for simulations, otherwise read by platform
Connections | Wärmeverbindung
length: |  |  | 50 | [m] | scalar
losses |  |  | 0.2 | [%/100m] | scalar
maxTransportCapacity |  |  | 999 | kW | scalar | or zero for no heat connection

## SF2_devices
Demand 1 | DEMND01 | Heat Demand
PrimSect |  |  | "heat" | - | string
DemandFC |  |  | time variable | kW | array
EffHtNetReceive |  |  | 0 | 1/(100m) | scalar | for heat network; 0 as no heat network
GrdBuyCost |  |  | 0 | €/kWh | array | for electric grid; 0 as this is heat demand
GrdSellCost |  |  | 0 | €/kWh | array | for electric grid; 0 as this is heat demand
GrdBuyCO2 |  |  | 0 | g/kWh | array | for electric grid; 0 as this is heat demand
GrdSellCO2 |  |  | 0 | g/kWh | array | for electric grid; 0 as this is heat demand
Demand 2 | DEMND02 | Electricity Demand
PrimSect |  |  | "elec" | [-] | string
DemandFC |  |  | time variable | kW | array
EffHtNetReceive |  |  | 0 | 1/(100m) | scalar | for heat network; 0 as this is electricity demand
GrdBuyCost |  |  | time variable | €/kWh | array | for electric grid
GrdSellCost |  |  | time variable | €/kWh | array | for electric grid
GrdBuyCO2 |  |  | 0 | g/kWh | array | for electric grid; 0 as CO2 optimization is not used
GrdSellCO2 |  |  | 0 | g/kWh | array | for electric grid; 0 as CO2 optimization is not used
Boiler | PROD01 | Gaskessel
PrimSect |  |  | "heat" | [-] | string
EffPrim |  |  | 0.88 | [-] | scalar
MinPower |  |  | 8 | kW | scalar
MaxPower |  |  | 20 | kW | scalar
GenCosts |  |  | time variable | €/kWh | array
CO2PerKWh |  |  | 0 | g/kWh | array | 0 as CO2 optimization is not used
Storage | STRGE01 | thermal storage
PrimSect |  |  | heat | [-] | string
Capacity |  |  | 62.94 | kWh | scalar | 773.6 l, T_max = 90°C, T_ref = 20°C, cp= 4.184 kJ/(kg*K), rho=100kg/m³
EffPrim |  |  | 0.97 | [-] | scalar
DisEffPrim |  |  | 0.97 | [-] | scalar
MaxPowerIn |  |  | 5 | kW | scalar
MaxPower |  |  | 5 | kW | scalar
StorLossPD |  |  | 0.021 | fraction of SOC per hour | scalar | cap = 62.94 kWh; losses = 24 kWh in 24 h beginning with 75% SOC
CO2PerKWh |  |  | -0.00012 | g/kWh | array
SOCminHOR |  |  | 0.5 | [-] | scalar | minimal SOC at end of horizon
PrimEnCost |  |  | 0 | €/kWh | scalar | not used
SOC_init |  |  | 0.5 | [-] | scalar | only for simulations, otherwise read by platform
Connections | Wärmeverbindung
length: |  |  | 50 | [m] | scalar
losses |  |  | 0.2 | [%/100m] | scalar
maxTransportCapacity |  |  | 999 | kW | scalar | or zero for no heat connection

## overview_timevariable
step / index | time [min] | time [h] | SF1_DEMND_heat | SF1_DEMND_elec | SF2_DEMND_heat | SF2_DEMND_elec | GenCosts | GrdBuyCosts | GrdSellCosts
0 | NaN | NaN
1 | 0 | 0 | 7.5385 | 0.75604 | 2.2 | 0.44087 | 0.07 | 0.3 | 0.1
2 | 15 | 0.25 | 7.5385 | 0.67276 | 13.2 | 1.992 | 0.07 | 0.3 | 0.1
3 | 30 | 0.5 | 4.3077 | 0.67766 | 8.8 | 4.2141 | 0.09 | 0.3 | 0.1
4 | 45 | 0.75 | 2.1538 | 2.0036 | 8.8 | 4.2952 | 0.09 | 0.3 | 0.1
5 | 60 | 1 | 5.3846 | 1.0369 | 4.4 | 2.1336 | 0.09 | 0.3 | 0.1
6 | 75 | 1.25 | 6.4615 | 2.8837 | 11 | 1.995 | 0.09 | 0.3 | 0.1
7 | 90 | 1.5 | 4.3077 | 3.9843 | 17.6 | 4.7051 | 0.09 | 0.3 | 0.1
8 | 105 | 1.75 | 2.1538 | 0.82952 | 0 | 3.3692 | 0.09 | 0.3 | 0.1
9 | 120 | 2 | 7.5385 | 1.0206 | 8.8 | 1.8682 | 0.07 | 0.3 | 0.1
10 | 135 | 2.25 | 14 | 0.89321 | 8.8 | 2.1926 | 0.07 | 0.3 | 0.1
11 | 150 | 2.5 | 1.0769 | 0.69399 | 2.2 | 0.58095 | 0.07 | 0.3 | 0.1
12 | 165 | 2.75 | 5.3846 | 3.1891 | 11 | 0.69449 | 0.07 | 0.3 | 0.1
13 | 180 | 3 | 7.5385 | 5 | 15.4 | 0.90239 | 0.07 | 0.3 | 0.1
14 | 195 | 3.25 | 1.0769 | 2.6878 | 6.6 | 1.3816 | 0.07 | 0.3 | 0.1
15 | 210 | 3.5 | 7.5385 | 0.80993 | 19.8 | 5 | 0.07 | 0.3 | 0.1
16 | 225 | 3.75 | 6.4615 | 0.73645 | 0 | 1.2784 | 0.07 | 0.3 | 0.1
17 | 240 | 4 | 4.3077 | 0.85402 | 0 | 3.1274 | 0.07 | 0.3 | 0.1
18 | 255 | 4.25 | 7.5385 | 0.95199 | 22 | 1.4126 | 0.07 | 0.3 | 0.1
19 | 270 | 4.5 | 10.7692 | 0.85238 | 11 | 0.97611 | 0.05 | 0.3 | 0.1
20 | 285 | 4.75 | 4.3077 | 0.83442 | 6.6 | 0.97611 | 0.05 | 0.25 | 0.03
21 | 300 | 5 | 1.0769 | 1.099 | 8.8 | 0.74462 | 0.05 | 0.25 | 0.03
22 | 315 | 5.25 | 4.3077 | 1.3374 | 8.8 | 0.92746 | 0.05 | 0.25 | 0.03
23 | 330 | 5.5 | 2.1538 | 1.2884 | 0 | 0.84046 | 0.05 | 0.25 | 0.03
24 | 345 | 5.75 | 3.2308 | 1.0304 | 11 | 1.0587 | 0.09 | 0.25 | 0.03
25 | 360 | 6 | 5.3846 | 1.0483 | 8.8 | 0.95252 | 0.09 | 0.25 | 0.03
26 | 375 | 6.25 | 4.3077 | 0.58459 | 6.6 | 1.4568 | 0.09 | 0.25 | 0.03
27 | 390 | 6.5 | 4.3077 | 0.65643 | 6.6 | 1.8593 | 0.09 | 0.25 | 0.03
28 | 405 | 6.75 | 3.2308 | 0.81973 | 8.8 | 0.81244 | 0.07 | 0.25 | 0.03
29 | 420 | 7 | 5.3846 | 1.3798 | 8.8 | 0.79917 | 0.07 | 0.25 | 0.03
30 | 435 | 7.25 | 4.3077 | 0.94056 | 2.2 | 0.80065 | 0.07 | 0.25 | 0.03
31 | 450 | 7.5 | 3.2308 | 1.2312 | 11 | 0.63108 | 0.07 | 0.25 | 0.03
32 | 465 | 7.75 | 3.2308 | 0.903 | 6.6 | 0.4969 | 0.07 | 0.25 | 0.03

## SF1_DEMND_heat
step / index | time [min] | time [h] | SF1_DEMND_heat
0 | NaN | NaN
1 | 0 | 0 | 7.5385 | kW
2 | 15 | 0.25 | 4.3077 | kW
3 | 30 | 0.5 | 2.1538 | kW
4 | 45 | 0.75 | 5.3846 | kW
5 | 60 | 1 | 6.4615 | kW
6 | 75 | 1.25 | 4.3077 | kW
7 | 90 | 1.5 | 2.1538 | kW
8 | 105 | 1.75 | 7.5385 | kW
9 | 120 | 2 | 14 | kW
10 | 135 | 2.25 | 1.0769 | kW
11 | 150 | 2.5 | 5.3846 | kW
12 | 165 | 2.75 | 7.5385 | kW
13 | 180 | 3 | 1.0769 | kW
14 | 195 | 3.25 | 7.5385 | kW
15 | 210 | 3.5 | 6.4615 | kW
16 | 225 | 3.75 | 4.3077 | kW
17 | 240 | 4 | 7.5385 | kW
18 | 255 | 4.25 | 10.7692 | kW
19 | 270 | 4.5 | 4.3077 | kW
20 | 285 | 4.75 | 1.0769 | kW
21 | 300 | 5 | 4.3077 | kW
22 | 315 | 5.25 | 2.1538 | kW
23 | 330 | 5.5 | 3.2308 | kW
24 | 345 | 5.75 | 5.3846 | kW
25 | 360 | 6 | 4.3077 | kW
26 | 375 | 6.25 | 4.3077 | kW
27 | 390 | 6.5 | 3.2308 | kW
28 | 405 | 6.75 | 5.3846 | kW
29 | 420 | 7 | 4.3077 | kW
30 | 435 | 7.25 | 3.2308 | kW
31 | 450 | 7.5 | 3.2308 | kW
32 | 465 | 7.75 | 5.3846 | kW

## SF1_DEMND_elec
step / index | time [min] | time [h] | SF1_DEMND_elec
0 | NaN | NaN
1 | 0 | 0 | 0.75604 | kW
2 | 15 | 0.25 | 0.67276 | kW
3 | 30 | 0.5 | 0.67766 | kW
4 | 45 | 0.75 | 2.0036 | kW
5 | 60 | 1 | 1.0369 | kW
6 | 75 | 1.25 | 2.8837 | kW
7 | 90 | 1.5 | 3.9843 | kW
8 | 105 | 1.75 | 0.82952 | kW
9 | 120 | 2 | 1.0206 | kW
10 | 135 | 2.25 | 0.89321 | kW
11 | 150 | 2.5 | 0.69399 | kW
12 | 165 | 2.75 | 3.1891 | kW
13 | 180 | 3 | 5 | kW
14 | 195 | 3.25 | 2.6878 | kW
15 | 210 | 3.5 | 0.80993 | kW
16 | 225 | 3.75 | 0.73645 | kW
17 | 240 | 4 | 0.85402 | kW
18 | 255 | 4.25 | 0.95199 | kW
19 | 270 | 4.5 | 0.85238 | kW
20 | 285 | 4.75 | 0.83442 | kW
21 | 300 | 5 | 1.099 | kW
22 | 315 | 5.25 | 1.3374 | kW
23 | 330 | 5.5 | 1.2884 | kW
24 | 345 | 5.75 | 1.0304 | kW
25 | 360 | 6 | 1.0483 | kW
26 | 375 | 6.25 | 0.58459 | kW
27 | 390 | 6.5 | 0.65643 | kW
28 | 405 | 6.75 | 0.81973 | kW
29 | 420 | 7 | 1.3798 | kW
30 | 435 | 7.25 | 0.94056 | kW
31 | 450 | 7.5 | 1.2312 | kW
32 | 465 | 7.75 | 0.903 | kW

## SF2_DEMND_heat
step / index | time [min] | time [h] | SF2_DEMND_heat
0 | NaN | NaN
1 | 0 | 0 | 2.2 | kW
2 | 15 | 0.25 | 13.2 | kW
3 | 30 | 0.5 | 8.8 | kW
4 | 45 | 0.75 | 8.8 | kW
5 | 60 | 1 | 4.4 | kW
6 | 75 | 1.25 | 11 | kW
7 | 90 | 1.5 | 17.6 | kW
8 | 105 | 1.75 | 0 | kW | o
9 | 120 | 2 | 8.8 | kW
10 | 135 | 2.25 | 8.8 | kW
11 | 150 | 2.5 | 2.2 | kW
12 | 165 | 2.75 | 11 | kW
13 | 180 | 3 | 15.4 | kW
14 | 195 | 3.25 | 6.6 | kW
15 | 210 | 3.5 | 19.8 | kW
16 | 225 | 3.75 | 0 | kW
17 | 240 | 4 | 0 | kW
18 | 255 | 4.25 | 22 | kW
19 | 270 | 4.5 | 11 | kW
20 | 285 | 4.75 | 6.6 | kW
21 | 300 | 5 | 8.8 | kW
22 | 315 | 5.25 | 8.8 | kW
23 | 330 | 5.5 | 0 | kW
24 | 345 | 5.75 | 11 | kW
25 | 360 | 6 | 8.8 | kW
26 | 375 | 6.25 | 6.6 | kW
27 | 390 | 6.5 | 6.6 | kW
28 | 405 | 6.75 | 8.8 | kW
29 | 420 | 7 | 8.8 | kW
30 | 435 | 7.25 | 2.2 | kW
31 | 450 | 7.5 | 11 | kW
32 | 465 | 7.75 | 6.6 | kW

## SF2_DEMND_elec
step / index | time [min] | time [h] | SF2_DEMND_elec
0 | NaN | NaN
1 | 0 | 0 | 0.44087 | kW
2 | 15 | 0.25 | 1.992 | kW
3 | 30 | 0.5 | 4.2141 | kW
4 | 45 | 0.75 | 4.2952 | kW
5 | 60 | 1 | 2.1336 | kW
6 | 75 | 1.25 | 1.995 | kW
7 | 90 | 1.5 | 4.7051 | kW
8 | 105 | 1.75 | 3.3692 | kW
9 | 120 | 2 | 1.8682 | kW
10 | 135 | 2.25 | 2.1926 | kW
11 | 150 | 2.5 | 0.58095 | kW
12 | 165 | 2.75 | 0.69449 | kW
13 | 180 | 3 | 0.90239 | kW
14 | 195 | 3.25 | 1.3816 | kW
15 | 210 | 3.5 | 5 | kW
16 | 225 | 3.75 | 1.2784 | kW
17 | 240 | 4 | 3.1274 | kW
18 | 255 | 4.25 | 1.4126 | kW
19 | 270 | 4.5 | 0.97611 | kW
20 | 285 | 4.75 | 0.97611 | kW
21 | 300 | 5 | 0.74462 | kW
22 | 315 | 5.25 | 0.92746 | kW
23 | 330 | 5.5 | 0.84046 | kW
24 | 345 | 5.75 | 1.0587 | kW
25 | 360 | 6 | 0.95252 | kW
26 | 375 | 6.25 | 1.4568 | kW
27 | 390 | 6.5 | 1.8593 | kW
28 | 405 | 6.75 | 0.81244 | kW
29 | 420 | 7 | 0.79917 | kW
30 | 435 | 7.25 | 0.80065 | kW
31 | 450 | 7.5 | 0.63108 | kW
32 | 465 | 7.75 | 0.4969 | kW

## GenCosts
step / index | time [min] | time [h] | GenCosts
0 | NaN | NaN
1 | 0 | 0 | 0.07 | €/kWh
2 | 15 | 0.25 | 0.07 | €/kWh
3 | 30 | 0.5 | 0.09 | €/kWh
4 | 45 | 0.75 | 0.09 | €/kWh
5 | 60 | 1 | 0.09 | €/kWh
6 | 75 | 1.25 | 0.09 | €/kWh
7 | 90 | 1.5 | 0.09 | €/kWh
8 | 105 | 1.75 | 0.09 | €/kWh
9 | 120 | 2 | 0.07 | €/kWh
10 | 135 | 2.25 | 0.07 | €/kWh
11 | 150 | 2.5 | 0.07 | €/kWh
12 | 165 | 2.75 | 0.07 | €/kWh
13 | 180 | 3 | 0.07 | €/kWh
14 | 195 | 3.25 | 0.07 | €/kWh
15 | 210 | 3.5 | 0.07 | €/kWh
16 | 225 | 3.75 | 0.07 | €/kWh
17 | 240 | 4 | 0.07 | €/kWh
18 | 255 | 4.25 | 0.07 | €/kWh
19 | 270 | 4.5 | 0.05 | €/kWh
20 | 285 | 4.75 | 0.05 | €/kWh
21 | 300 | 5 | 0.05 | €/kWh
22 | 315 | 5.25 | 0.05 | €/kWh
23 | 330 | 5.5 | 0.05 | €/kWh
24 | 345 | 5.75 | 0.09 | €/kWh
25 | 360 | 6 | 0.09 | €/kWh
26 | 375 | 6.25 | 0.09 | €/kWh
27 | 390 | 6.5 | 0.09 | €/kWh
28 | 405 | 6.75 | 0.07 | €/kWh
29 | 420 | 7 | 0.07 | €/kWh
30 | 435 | 7.25 | 0.07 | €/kWh
31 | 450 | 7.5 | 0.07 | €/kWh
32 | 465 | 7.75 | 0.07 | €/kWh

## GrdBuyCost
step / index | time [min] | time [h] | GrdBuyCosts
0 | NaN | NaN
1 | 0 | 0 | 0.3 | €/kWh
2 | 15 | 0.25 | 0.3 | €/kWh
3 | 30 | 0.5 | 0.3 | €/kWh
4 | 45 | 0.75 | 0.3 | €/kWh
5 | 60 | 1 | 0.3 | €/kWh
6 | 75 | 1.25 | 0.3 | €/kWh
7 | 90 | 1.5 | 0.3 | €/kWh
8 | 105 | 1.75 | 0.3 | €/kWh
9 | 120 | 2 | 0.3 | €/kWh
10 | 135 | 2.25 | 0.3 | €/kWh
11 | 150 | 2.5 | 0.3 | €/kWh
12 | 165 | 2.75 | 0.3 | €/kWh
13 | 180 | 3 | 0.3 | €/kWh
14 | 195 | 3.25 | 0.3 | €/kWh
15 | 210 | 3.5 | 0.3 | €/kWh
16 | 225 | 3.75 | 0.3 | €/kWh
17 | 240 | 4 | 0.3 | €/kWh
18 | 255 | 4.25 | 0.3 | €/kWh
19 | 270 | 4.5 | 0.3 | €/kWh
20 | 285 | 4.75 | 0.25 | €/kWh
21 | 300 | 5 | 0.25 | €/kWh
22 | 315 | 5.25 | 0.25 | €/kWh
23 | 330 | 5.5 | 0.25 | €/kWh
24 | 345 | 5.75 | 0.25 | €/kWh
25 | 360 | 6 | 0.25 | €/kWh
26 | 375 | 6.25 | 0.25 | €/kWh
27 | 390 | 6.5 | 0.25 | €/kWh
28 | 405 | 6.75 | 0.25 | €/kWh
29 | 420 | 7 | 0.25 | €/kWh
30 | 435 | 7.25 | 0.25 | €/kWh
31 | 450 | 7.5 | 0.25 | €/kWh
32 | 465 | 7.75 | 0.25 | €/kWh

## GrdSellCost
step / index | time [min] | time [h] | GrdSellCosts
0 | NaN | NaN
1 | 0 | 0 | 0.1 | €/kWh
2 | 15 | 0.25 | 0.1 | €/kWh
3 | 30 | 0.5 | 0.1 | €/kWh
4 | 45 | 0.75 | 0.1 | €/kWh
5 | 60 | 1 | 0.1 | €/kWh
6 | 75 | 1.25 | 0.1 | €/kWh
7 | 90 | 1.5 | 0.1 | €/kWh
8 | 105 | 1.75 | 0.1 | €/kWh
9 | 120 | 2 | 0.1 | €/kWh
10 | 135 | 2.25 | 0.1 | €/kWh
11 | 150 | 2.5 | 0.1 | €/kWh
12 | 165 | 2.75 | 0.1 | €/kWh
13 | 180 | 3 | 0.1 | €/kWh
14 | 195 | 3.25 | 0.1 | €/kWh
15 | 210 | 3.5 | 0.1 | €/kWh
16 | 225 | 3.75 | 0.1 | €/kWh
17 | 240 | 4 | 0.1 | €/kWh
18 | 255 | 4.25 | 0.1 | €/kWh
19 | 270 | 4.5 | 0.1 | €/kWh
20 | 285 | 4.75 | 0.03 | €/kWh
21 | 300 | 5 | 0.03 | €/kWh
22 | 315 | 5.25 | 0.03 | €/kWh
23 | 330 | 5.5 | 0.03 | €/kWh
24 | 345 | 5.75 | 0.03 | €/kWh
25 | 360 | 6 | 0.03 | €/kWh
26 | 375 | 6.25 | 0.03 | €/kWh
27 | 390 | 6.5 | 0.03 | €/kWh
28 | 405 | 6.75 | 0.03 | €/kWh
29 | 420 | 7 | 0.03 | €/kWh
30 | 435 | 7.25 | 0.03 | €/kWh
31 | 450 | 7.5 | 0.03 | €/kWh
32 | 465 | 7.75 | 0.03 | €/kWh